**SECTION 15834 [23 34 33] – AIR CURTAINS**

***NOTE TO SPECIFICATION AUTHOR:*** *Enable “Hidden Text” under File>Options>Display. Green text in [] indicates options that the specification author needs to select prior to completion of the Contract Document specifications. Enable “Navigation Pane” under “View” tab for easy browsing. Delete this text box after viewing.*

# PART 1 - GENERAL

## SUMMARY:

1. This section includes [electric heated] air curtains.

## RELATED REQUIREMENTS: ***NOTE TO SPECIFICATION AUTHOR:*** *Delete requirements not relevant to specification.*

1. Section 04 22 00 - Concrete Unit Masonry
2. Section 05 40 00 - Cold-Formed Metal Framing
3. Section 05 50 00 – Metal Fabrications
4. Section 06 10 00 - Rough Carpentry
5. Section 08 11 00 - Metal Doors and Frames
6. Section 08 33 23 – Overhead Coiling Doors
7. Section 08 41 00 - Entrances and Storefronts
8. Section 08 71 00 - Door Hardware
9. Section 09 22 16 – Non-Structural Metal Framing
10. Section 09 51 13 – Acoustical Panel Ceilings
11. Section 09 91 00 – Painting
12. Division 22 – Plumbing
13. Division 23 - Heating, Ventilating, and Air-Conditioning (HVAC)
14. Division 26 - Electrical

## REFERENCE STANDARDS:

1. AMCA 211 - Certified Ratings Program - Product Rating Manual for Fan Air Performance.
2. AMCA 220 - Laboratory Methods of Testing Air Curtain Units for Aerodynamic Performance Ratings.
3. AMCA 222 - Application Manual for Air Curtain Units.
4. ARI 410 - Forced-Circulation Air-Cooling and Air-Heating Coils.
5. ASHRAE 135 - BACnet - A Data Communication Protocol for Building Automation and Control Networks.
6. NEMA 250 - Enclosures for Electrical Equipment (1000 Volts Maximum).
7. NSF 37 - Air Curtains for entranceways in food and foodservice establishments - ETL Sanitation
8. UL 507 - Electric Fans.
9. UL 1995 - Heating and Cooling Equipment
10. UL 2021 - Fixed and Location-Dedicated Electric Room Heaters.

## SUBMITTALS:

1. Submittals under the provisions of Section [01 33 00] are required to show full compliance with the contract documents.

### Product Data:

1. Product Data must have the specific Contract Document air curtain mark/tag on each submittal with all information associated with each unit clearly identified. Where information does not apply to the product being provided, then such information must be marked off on the submittal.
2. Rated capacities showing compliance with Contract Document requirements scheduled on drawings. Capacities including but not limited to: Airflow (CFM), discharge velocity (FPM), noise rating (dBA), motor quantity and horsepower, electrical ratings (FLA, volts/phase/hertz), outlet velocity uniformity (%), unit assembly weight (lbs.).
3. Mechanical Drawings.
4. Wiring Diagrams.
5. Standard product features.
6. Optional product features and accessories.

### Shop Drawings:

1. Provide drawings showing air curtain assembly and parts.
2. Wiring Diagrams: Power, signal, and control wiring. The wiring diagram must indicate a clear distinction between manufacturer’s factory furnished and installed wiring, and contractor furnished and installed wiring for all power, signal and control wiring and accessories.
3. Installation Instructions: Manufacturer’s installation instructions with diagrams, instructions, and manufacturer’s contact information
4. Operation and Maintenance Data: Complete documentation of manufacturer’s recommended operation and maintenance procedures for the air curtain including commissioning procedures.
5. Manufacturer’s Warranty statement for products and parts.
6. Contractor’s Warranty statement for repair and replacement of products and parts.

## QUALITY ASSURANCE:

1. Comply with all applicable ordinances, codes and standards required by the authorities having jurisdiction.
2. Comply with NFPA 70 - National Electrical Code.
3. ETL Listed (Tested in accordance with UL 1995, 4th Edition, dated October 14, 2011, including revisions through October 3, 2014, and CSA C22.2 No. 236-11, 4th Edition, dated October 14, 2011, including revisions through October 3, 2014).
4. All units tested in accordance with ANSI/AMCA 220. Unheated units shall bear AMCA Seal for Performance.
5. UL and cUL listed to comply with applicable United States and Canadian standards.
6. Obtain each type of air curtain through one (1) source from a single manufacturer.

## COORDINATION:

1. Coordinate layout and installation of air curtains, mounting system and all components associated with the air curtains with other construction.
2. Notify the architect/engineer of any coordination conflicts prior to installation of the air curtain or other associated parts and accessories so that the installation can be coordinated prior to installation.
3. Any installation commenced or completed without coordination is subject to rejection of the work and must be redone as required to meet the intent of the contract documents.

## DELIVERY, STORAGE AND HANDLING:

1. Supply air curtains in original, clearly labeled packaging as provided by the manufacturer.
2. Store and handle equipment in full accordance with the manufacturer's documented guidelines and best practices.
3. Ensure protection of units from environmental damage, including exposure to weather, extreme temperatures, and ongoing construction activities.

## WARRANTY:

1. Manufacturer’s standard warranty for replacement of parts for a period of (60 months for unheated units and 24 months for heated units) from the time of shipment from the manufacturer.
2. The warranty shall extend to and cover all parts, components, accessories, and associated equipment supplied with the air curtain, regardless of whether such parts, components, or accessories are manufactured directly by the air curtain manufacturer or by third-party suppliers.

# PART 2 - PRODUCTS

## MANUFACTURER[S]:

1. Basis-Of-Design Manufacturer: All air curtains furnished are complete factory assembled units as manufactured by Powered Aire Inc., 109 Mortensen Road, Greenville, PA – 16125

Phone: 1-888-321-2473

Website: [www.PoweredAire.com](http://www.PoweredAire.com)

1. Substitutions are not permitted. ***NOTE TO SPECIFICATION AUTHOR:*** *Replace with “Substitutions will be considered under the provisions of Section 01 60 00.” if relevant.*

## BASIC EQUIPMENT DESCRIPTION:

1. Each air curtain unit consists of a factory assembled metal casing, tangential fans, inlet screen, discharge nozzle, and motor(s). Additional optional accessories as specified.
2. The air curtain must be interlocked with the door, this could be by a door switch, through dry contacts in the door controller or by other means.
3. Units shall be furnished in single increments of sufficient structural strength to be supported from the top or back per manufacturer’s instructions.

## CASING:

1. Materials: 18 GA Steel.
2. Finish: Brushed Stainless Steel

## AIR INLET:

1. Inlet screen shall be hole pattern punched 18 GA Steel with finish matching the case.

## AIR DISCHARGE NOZZLE:

1. Discharge nozzle shall be high efficiency discharge plenum. Air curtain creates a positive air seal with an adjustable air foil vane. The vane shall facilitate a deflection of the air stream by +/- 20 degrees.

## MOTOR:

1. Type: 107W, 3000 RPM PSC Motor, resiliently mounted, continuous duty.
2. Bearings: Heavy duty type permanently lubricated, shielded ball bearings of equal size.

## FANS:

1. Balanced, Aluminum, forward curved tangential type with flexible hubs.

## OPTIONAL HEATING: ***NOTE TO SPECIFICATION AUTHOR:*** *Delete Section 2.8 for unheated units.*

### Electric Heat:

1. Factory mounted electric heating elements mounted on Galvanized steel frame, inside the air curtain plenum on the discharge side of the blowers.
2. Helical coil with point suspension of elements.
3. Single point power connection and control wiring to the air curtain.
4. Automatic reset thermal overloads, contactor interlock.

## ACCESSORIES:

1. Activation Options: ***NOTE TO SPECIFICATION AUTHOR:*** *Optional accessory to be specified.*
2. [Automatic Magnetic Window Switch Kit]: Remotely installed in the door area to activate or deactivate the air curtain unit as per door position. Includes Time delay relay to extend operation time from 1s to 100s after door closing.
3. Manual Switches:
4. Fan/OFF/Heat: Unit mounted. Set unit to Fans only, OFF or Fans with Heat. ***NOTE TO SPECIFICATION AUTHOR:*** *Delete for unheated air curtains.*
5. Variable Speed Switch: Unit mounted Variable Speed Switch to vary speed from Min to Max or OFF.
6. Mounting Brackets:
7. Swivel mounting brackets allow for rear or top mounting and allow for adjustment of the discharge.

# PART 3 - EXECUTION

## EXAMINATION:

1. Examine the installation location where each air curtain will be installed to confirm that the installation location is in accordance with the Contract Documents and the Manufacturer’s Installation Instructions.
2. If there are any concerns regarding the installation location with respect to any aspect of the installation or performance of the air curtain notify the architect/engineer to resolve the concern.

## INSTALLATION:

1. Install each air curtain in accordance with the Installation Instructions provided by the manufacturer of the air curtain.
2. Ensure sufficient clearance is provided at the front and bottom of the air curtain for maintenance and service.
3. Install activation accessories and control switches (if present) as per drawings.

## FIELD QUALITY CONTROL:

1. Perform the following field tests and inspections and prepare test reports:
2. After installing air curtains completely, perform visual and mechanical check of individual components.
3. After electrical circuitry has been energized, start unit to confirm motor rotation and the unit operates as intended.
4. Test and adjust controls and safety.
5. Adjust air-directional vanes such that the airflow covers the door opening.
6. Contact air curtain manufacturer in case of damaged or malfunctioning controls & equipment.

## CLEANING:

1. Clean the outside of each air curtain of any dirt, debris, grease, grime, or other material.
2. Remove any loose debris, dirt or grease on the inside, which may be harmful to the air curtain operation.

## DEMONSTRATION:

1. Contractor to instruct the Owner's maintenance personnel on how to adjust, operate, and maintain air curtains.

## MECHANICAL SCHEDULES:

1. Unheated:

Performance: <https://poweredaire.com/assets/downloads/air-curtain/ptw/ptw_data_table.pdf>

1. Electric Heat:

Performance: <https://poweredaire.com/assets/downloads/air-curtain/ptw-e/ptw-e_data_table.pdf>

END OF SECTION