Powered Aire, Inc. Model EHD IG & DG Basis-Of-Design Guide Specification

NOTE TO SPECIFICATION WRITER:  Green  text in [] indicates options that the design engineer needs to select prior to completion of the Contract Document specifications.  This text needs to be edited as appropriate and deleted if not desired in the specification.

SECTION 15834 [23 34 33]  – AIR CURTAINS

PART 1 -GENERAL

  - SUMMARY:

- This Section includes air curtains.

  - DEFINITIONS:

- For convenience purposes a few definitions are indicated herein.  All capacities, ratings and other specified and scheduled air curtain criteria are based on these definitions.

1. 	Air Curtain:  An air moving device which produces a directionally-controlled airstream, moving across the entire height and width of an opening.

2. 	Unit Airflow Rate:  The airflow volume which leaves the discharge nozzle, at standard air conditions, and reported in CFM.

3.  	Average Outlet Velocity:  The airflow rate produced by the air curtain divided by the cross sectional area of the discharge nozzle plane at free-air delivery, and reported in FPM.

4.  	Outlet Air Velocity Uniformity:  An indicator of the consistency of air velocities across the air curtain width, expressed as a percentage.

5.  	Air Discharge Angle:  The angle between the plane of the protected opening and the direction in which the air stream leaves the discharge.

  - SYSTEM DESCRIPTION:

A.	An air curtain is an air moving device which produces a directionally-controlled airstream, moving across the entire height and width of an opening.

  - SUBMITTALS:

- Submittals are required to show full compliance with the contract documents.

- Indicate each air curtain tag/mark number on the submittal as applicable.

- Product Data:

1.	Product Data must have the specific Contract Document air curtain mark/tag on each submittal with all information associated with each unit clearly identified.  Where information does not apply to the product being provided then such information must be marked off on the submittal.

2.	Rated capacities showing compliance with Contract Document requirements scheduled on drawings.  Capacities including but not limited to: Airflow (CFM), discharge velocity (FPM), noise rating (dBA), motor quantity and horsepower, electrical ratings (FLA, volts/phase/hertz), outlet velocity uniformity (%), unit assembly weight (lbs).

3.	Mechanical Drawings.

4.	Wiring Diagrams.

5.	Standard product features.

6.	Optional product features and accessories.

- Shop Drawings:

- Provide drawings showing air curtain assembly and parts.

- Wiring Diagrams: Power, signal, and control wiring.   The wiring diagram must indicate a clear distinction between manufacturer’s factory furnished and installed wiring, and contractor furnished and installed wiring for all power, signal and control wiring and accessories.

- Installation Instructions:  Manufacturer’s installation instructions with diagrams, instructions and manufacturer’s contact information.

- Operation and Maintenance Data:  Complete documentation of manufacturer’s recommended operation and maintenance procedures for the air curtain including commissioning procedures.

- Manufacturer’s Warranty statement for products and parts.

- Contractor’s Warranty statement for repair and replacement of products and parts.

  - QUALITY ASSURANCE:

- The Contract Document Drawings and Specifications indicate the “basis-of-design” manufacturer, model, size, profiles, and dimensional requirements of air curtains.

- Comply with all applicable ordinances, codes and standards as required by the authorities having jurisdiction.

- Comply with NFPA 70 - National Electrical Code.

  - COORDINATION:

- Coordinate layout and installation of air curtains, mounting system and all components associated with the air curtains with other construction.

B.	Notify the architect/engineer of any coordination conflicts prior to installation of the air curtain or other associated parts and accessories so that the installation can be coordinated prior to installation.  Any installation that is commenced or completed without coordination is subject to rejection of the work and must be redone as required to meet the intent of the contract documents.

  - WARRANTY:

- Provide manufacturer’s standard warranty for replacement of parts for a period of 18 months from the time of shipment from the manufacturer.  The warranty must cover all parts, components, accessories, etc. provided with the air curtain whether or not the parts, components or accessories are the direct product manufactured by the air curtain manufacturer.

PART 2 -PRODUCTS

  - MANUFACTURER[S]:

- Basis-Of-Design Manufacturer:

1.	All air curtains furnished are complete factory assembled units as manufactured by Powered Aire Inc.

Address:  109 Mortensen Road, Greenville, PA   16125

Toll Free Phone:  1-888-321-2473

- [Other Acceptable Manufacturers: Subject to compliance with requirements of the Contract Documents

Other Acceptable Manufacturers must show full compliance with the intent of the basis-of-design

manufacturer model’s performance as well as all other specified features and characteristics.  A line-by-line comparison of any variances from any of the basis-of-design performance, features or characteristics must be provided by the other acceptable manufacturers with a clear explanation of how the other acceptable manufacturer’s unit meets or exceeds the intent of the basis-of-design specified unit make and model.]

    - [The engineer may list another manufacturer of air curtains here.]

    - [The engineer may list another manufacturer of air curtains here.]

    - [The engineer may list another manufacturer of air curtains here.]

2.02         EQUIPMENT BASIC DESCRIPTION – BASIS-OF-DESIGN

A.	Each unit consists of a factory assembled casing, centrifugal fans, discharge nozzle, motor(s), and access panels for motor and fan assembly.  Additional accessories as specified.  The air curtain provides a specific CFM and a uniform outlet velocity across the entire length of the discharge nozzle area. A remote (for Indirect Gas) and unit (for direct gas) mounted Nema 12 control panel will be provided.

2.03	AIR CURTAIN CASING:

- Housing Materials:  Top and Bottom access panels shall be a minimum 16 gauge stainless steel.

B.	Unit Support:  Integral to the unit frame or casing.   All weight bearing structural support shall be formed 11-gauge stainless steel and galvanized steel.  Units shall be furnished in single increments of sufficient structural strength to be supported from the top per manufacturer’s instructions.

  - AIR DISCHARGE NOZZLE

A.	Discharge nozzle shall be high efficiency discharge plenum.  Air curtain creates a positive air seal with directional air foil vanes.  The vanes shall facilitate a deflection of the air stream by +/- 20 degrees.

  - FANS

- Wheels and Housings: Dynamically balanced curved double inlet double width galvanized blower wheels with brazed hubs and matched blower housings.

- Drives: Direct Drive.   Belt Drive Not Acceptable.

  - MOTORS:

- Type:  Total Enclosed Air Over (TEAO) continuous duty.

- Bearings: Heavy duty type, shielded ball bearings of equal size.

2.07	 [INDIRECT GAS HEATER AND DUCT TRANSITION]

A.	American Gas Association (AGA) or Canadian Gas Association (CGA) labeled.

B.	Gas Heater Equipped with: Power Exhaust, Direct Spark Ignition, Electronic Flame Supervision, 24 Volt Control Transformer,   Self-Diagnostic Control Board, and Gas Pressure Switches.

C.	Tubular Heat Exchangers: [Aluminized Steel, Stainless Steel]

D.	Heater to be independently supported 2 inches from each opening of factory-installed duct transition.

E.	Duct Transition constructed of 18 gauge stainless steel.

F.	Fuel Type: [Natural Gas, Propane]

2.08	[DIRECT GAS FIRED HEATER]

A.	Fuel Type: [Natural Gas, Propane].

B.	Direct Gas Heater Equipped with: Minimum Turndown Ratio of 30:1 Stainless Steel Baffles, Non-Clogging Orifices, Ignition System, Flame Safeguard, Gas Manifold, Valves, and Temperature Controls.

C.	Gas Train: As Required by IRI.

D.	Spark Ignited Intermittent Pilot.

  - [ACCESSORIES] (Please include on schedule)

A.	Control Panel:  To house the controls. [unit mounted for EHD DG, remote mounted EHD IG]

B.	Disconnect: [remote mounted, panel mounted], [fused, non-fused]

C.	Automatic Door Switch:  Remotely installed in the door area to activate the unit each time the door opens and deactivate the unit each time the door closes.

D.	Adjustable Time Delay:  Integral part of the panel, only used with an automatic door switch.  Air curtain to operate until specified time (adjustable from 1.0 to 100 seconds) after the door closes.

E.	Hand/Off/Auto Switch: (Available with all indirect gas fired. Only available with direct gas fired if intake is ducted to outside)  Acts as an override to the automatic door switch.  In Hand position the air curtain is on, in Off position the air curtain is off, and in Auto position the air curtain runs via the automatic door switch.  [remote mounted, panel mounted]

F.            Thermostat: Turns heaters on and off according to temperature. [line voltage, low voltage], [remote mounted, panel mounted]

PART 3 -EXECUTION

  - EXAMINATION:

- Examine the installation location where each air curtain will be installed to confirm that the installation location is in accordance with the Contract Documents and the Manufacturer’s Installation Instructions.

- If there are any concerns regarding the installation location with respect to any aspect of the installation or performance of the air curtain notify the architect/engineer in order to resolve the concern.

  - INSTALLATION:

- Install each air curtain in accordance with the Installation Instructions provided by the manufacturer of the air curtain.

  - SYSTEM STARTUP

- Startup each air curtain in accordance with the manufacturer’s Operations and Maintenance Manual and Installation Instructions.

  - FIELD QUALITY CONTROL:

- Perform the following field tests and inspections and prepare test reports:

- After installing air curtains completely, perform visual and mechanical check of individual components.

- After electrical circuitry has been energized, start unit to confirm motor rotation and unit operation.

- Test and adjust controls and safeties. Replace damaged and malfunctioning controls and equipment.

- Repair or replace malfunctioning units and retest as specified above.

  - ADJUSTING:

- Adjust air-directional vanes.

  - CLEANING:

- Clean the outside of each air curtain of any dirt, debris, grease, grime or other material.

- Clean the inside of each air curtain of any dirt, debris, grease, grime or other material as necessary to ensure proper operation.  Remove any loose debris that may be of harm to the air curtain operation.

  - DEMONSTRATION:

- Contractor to instruct the Owner's maintenance personnel on how to adjust, operate, and maintain air curtains.

  - SCHEDULE:

INDIRECT GAS FIRED AIR CURTAIN SCHEDULE

| Mark | Basis- Of- Design Manufacturer | Model | Airflow Rate At Nozzle Outlet (CFM) | Average Outlet Velocity (FPM) | Outlet Velocity Uniformity (%) | Motor (Quantity @ HP) | Door Width | Indirect Gas Input mbtu/hr # of per Heaters heater |  | Temp. Rise (F) | Motor Voltage (V/Ph/Hz) | Sound Level (dBA) on High | Notes |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| AC1 | Powered Aire | EHD IG |  |  |  | [1,2,3,4] @ 5 |  |  |  |  |  | 71 | (1) (2) |
| AC2 | Powered Aire |  |  |  |  |  |  |  |  |  |  |  | (1) (2) |
| AC3 | Powered Aire |  |  |  |  |  |  |  |  |  |  |  |  |
| AC4 | Powered Aire |  |  |  |  |  |  |  |  |  |  |  |  |

Notes:

- Sound Level is measured 10 feet from the air curtain in a free field based on a one motor unit.

- The specification requirements for these accessories are as indicated in the Air Curtain section of the Specification section of these Contract Documents.  Provide the following accessories for this unit: [Control Panel, Disconnect, Automatic Door Switch, Adjustable Time Delay, Hand/Off/Auto Switch, Thermostat]

DIRECT GAS FIRED AIR CURTAIN SCHEDULE

| Mark | Basis- Of- Design Manufacturer | Model | Airflow Rate At Nozzle Outlet (CFM) | Average Outlet Velocity (FPM) | Outlet Velocity Uniformity (%) | Motor (Quantity @ HP) | Door Width | Maximum Btu | Maximum Temperature Rise | Motor Voltage (V/Ph/Hz) | Sound Level (dBA) on High | Notes |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| AC1 | Powered Aire | EHD DG |  |  |  | [1,2,3] @ 5 |  |  | [105] |  | 71 | (1) (2) |
| AC2 | Powered Aire |  |  |  |  |  |  |  |  |  |  | (1) (2) |
| AC3 | Powered Aire |  |  |  |  |  |  |  |  |  |  |  |
| AC4 | Powered Aire |  |  |  |  |  |  |  |  |  |  |  |

Notes:

(1)	Sound Level is measured 10 feet from the air curtain in a free field based on a one motor unit.

(2)   The specification requirements for these accessories are as indicated in the Air Curtain section of the Specification section of these Contract Documents.  Provide the following

accessories for this unit: [Control Panel, Disconnect, Automatic Door Switch, Adjustable Time Delay, Hand/Off/Auto Switch (only if intake is ducted to the outside), Thermostat]

END OF SECTION 15834 [23 34 33]